## Factors
Low Pressure PE80 or PE100 | [5 empty] | Medium Pressure PE80 or PE100 | [5 empty] | Intermediate Pressure PE100 |  |  |  | Steel Pipe to GIS/L2
Dia (mm) | SDR11 | SDR13.6 | SDR17.6 | SDR21 | SDR26 | Dia (mm) | SDR11 | SDR13.6 | SDR17.6 | SDR21 | SDR26 | Dia (mm) | IP 6/4bar SDR11 | IP 7/5.5bar SDR11 | IP 7/7bar SDR11 | Dia (mm) | NPS (inches) | Low pressure MOP 75mbar | Medium pressure MOP 2bar | Intermediate Pressure (6/4) MOP 4 bar | Intermediate Pressure (7/5.5) MOP 5.5 bar | Intermediate Pressure (7/7) MOP 7 bar
32 | 0.00015 |  |  |  |  | 32 | 0.0004 |  |  |  |  | 55 | 0.0013 | 0.0018 | 0.0028 | 25 | 1 | 0.0002 | 0.0005 | 0.0004 | 0.0006 | 0.0009
40 | 0.00024 |  | 0.0003 |  |  | 40 | 0.0007 |  | 0.0009 |  |  | 63 | 0.0018 | 0.0023 | 0.0037 | 32 | 1.25 | 0.0003 | 0.0008 | 0.0008 | 0.001 | 0.0016
55 | 0.00048 |  | 0.00054 |  |  | 55 | 0.0014 |  | 0.0016 |  |  | 75 | 0.0025 | 0.0033 | 0.0052 | 40 | 1.5 | 0.0004 | 0.0011 | 0.0011 | 0.0014 | 0.0022
63 | 0.00063 | 0.00068 | 0.00072 |  |  | 63 | 0.0018 | 0.002 | 0.0022 |  |  | 90 | 0.0036 | 0.0048 | 0.0075 | 50 | 2 | 0.0007 | 0.0018 | 0.0017 | 0.0023 | 0.0036
75 | 0.0009 | 0.00096 | 0.00102 |  |  | 75 | 0.0025 | 0.0028 | 0.0031 |  |  | 110 | 0.0053 | 0.0071 | 0.0111 | 80 | 3 | 0.0016 | 0.0043 | 0.0041 | 0.0055 | 0.0086
90 | 0.00129 |  | 0.0015 | 0.00156 |  | 90 | 0.0037 |  | 0.0044 | 0.0046 |  | 125 | 0.0069 | 0.0092 | 0.0144 | 100 | 4 | 0.0028 | 0.0074 | 0.0071 | 0.0094 | 0.0147
110 |  |  |  | 0.00234 |  | 110 |  |  |  | 0.0068 |  | 140 | 0.0087 | 0.0115 | 0.018 | 150 | 6 | 0.0064 | 0.0171 | 0.0164 | 0.0218 | 0.0341
125 | 0.00246 |  | 0.00288 |  |  | 125 | 0.0072 |  | 0.0085 |  |  | 160 | 0.0113 | 0.0151 | 0.0236 | 200 | 8 | 0.0111 | 0.0295 | 0.0281 | 0.0375 | 0.0586
140 |  |  | 0.0036 |  | 0.00393 | 140 |  |  | 0.0106 |  | 0.0115 | 180 | 0.0143 | 0.0191 | 0.0298 | 250 | 10 | 0.0176 | 0.0469 | 0.0447 | 0.0597 | 0.0932
160 |  |  | 0.00471 |  | 0.00513 | 160 |  |  | 0.0139 |  | 0.0151 | 200 | 0.0177 | 0.0236 | 0.0368 | 300 | 12 | 0.0251 | 0.067 | 0.0639 | 0.0853 | 0.1332
180 | 0.0051 |  | 0.00594 |  |  | 180 | 0.015 |  | 0.0176 |  |  | 213 | 0.02 | 0.0267 | 0.0417 | 400 | 16 | 0.0395 | 0.1054 | 0.1006 | 0.1341 | 0.2095
200 |  |  | 0.00735 |  | 0.00804 | 200 |  |  | 0.0217 |  | 0.0235 | 250 | 0.0276 | 0.0368 | 0.0575 | 450 | 18 | 0.0504 | 0.1344 | 0.1283 | 0.1711 | 0.2673
213 |  |  |  |  | 0.00912 | 213 |  |  |  |  | 0.0267 | 268 | 0.0317 | 0.0423 | 0.0661 | 600 | 24 | 0.0915 | 0.2439 | 0.2328 | 0.3104 | 0.485
225 |  |  |  |  | 0.01017 | 225 |  |  |  |  | 0.0298 | 280 | 0.0346 | 0.0462 | 0.0721 | 750 | 30 | 0.1431 | 0.3816 | 0.3642 | 0.4856 | 0.7588
250 | 0.00987 |  | 0.01146 | 0.01206 |  | 250 | 0.0289 |  | 0.0339 | 0.0354 |  | 315 | 0.0438 | 0.0584 | 0.0913 | 900 | 36 | 0.2054 | 0.5478 | 0.5229 | 0.6972 | 1.0893
268 |  |  |  |  | 0.01443 | 268 |  |  |  |  | 0.0423 | 355 | 0.0557 | 0.0742 | 0.116 | 1050 | 42 | 0.2812 | 0.7499 | 0.7159 | 0.9545 | 1.4914
280 |  |  |  |  | 0.01575 | 280 |  |  |  |  | 0.0462 | 400 | 0.0707 | 0.0942 | 0.1472 | 1200 | 48 | 0.3673 | 0.9795 | 0.935 | 1.2467 | 1.9479
315 | 0.01566 |  | 0.01821 | 0.01914 | 0.01992 | 315 | 0.0459 |  | 0.0539 | 0.0561 | 0.0584 | 450 | 0.0894 | 0.1192 | 0.1863 | – Test period for Steel Pipe (manufactured to GIS/L2:2006) for both Low and Medium Pressure per metre length (calculated in hours) Maximum pressure loss 3mbar
355 | 0.01989 |  | 0.02313 | 0.0243 |  | 355 | 0.0583 |  | 0.0684 | 0.0713 |  | 469 | 0.0971 | 0.1295 | 0.2024
400 | 0.02523 |  | 0.02934 | 0.03087 |  | 400 | 0.074 |  | 0.0869 | 0.0905 |  | 500 | 0.1104 | 0.1472 | 0.23
440 |  |  |  |  | 0.03888 | 440 |  |  |  |  | 0.114 | 630 | 0.1753 | 0.2337 | 0.3652
450 | 0.03195 |  | 0.03714 | 0.03906 |  | 450 | 0.0937 |  | 0.11 | 0.1146 |  | Test period table for Intermediate Pressure PE100 mains per metre length (calculated in hours) Maximum allowable pressure loss = 3 mbar + any additional creep allowance.
469 |  |  |  | 0.04242 |  | 469 |  |  |  | 0.1244
500 | 0.03942 |  | 0.04587 | 0.04821 |  | 500 | 0.1157 |  | 0.1357 | 0.1414
560 |  |  |  |  | 0.06297 | 560 |  |  |  |  | 0.1847
630 | 0.06261 |  | 0.07281 | 0.07656 |  | 630 | 0.1836 |  | 0.2155 | 0.2246
Test period table for Low Pressure PE80 and PE100 mains per metre length (calculated in hours) | [5 empty] | Test period table for Medium Pressure PE80 and PE100 mains per metre length (calculated in hours) Maximum allowable pressure loss = 3 mbar + any additional creep allowance.

## Test_using_Factors
Single pipe
Size | Length | SDR | Factor |  | Time H/M | Conditioning Period |  | Conditioning Time |  | Total Test Time
315 | 2800 | 11 | 0.01933 | 54.124 | 54:07 | 2.3 | 23.5322 | 23:31 | 77.6562 | 77:39
Multiple PE pipe sizes Same SDR
Size | Length | SDR | Factor |  | Time H/M | Conditioning Period |  | Conditioning Time |  | Total Test Time
250 | 10100 | 17.6 | 0.0339 | 342.39 | 342:23
315 | 2300 | 17.6 | 0.0539 | 123.97 | 123:58
|  |  |  | 0 | 00:00
|  |  |  | 466.36 | 466:21 | 4.9 | 95.1755 | 95:10 | 561.5355 | 561:32
Multiple same size pipe different SDR's
Size | Length | SDR | Factor |  | Time H/M | Conditioning Period |  | Conditioning Time |  | Total Test Time
180 | 500 | 11 | 0.015 | 7.5 | 07:30
180 | 1232 | 17.6 | 0.0176 | 21.6832 | 21:41
|  |  |  | 29.1832 | 29:11 | 4.8 | 6.0798 | 06:04 | 35.263 | 35:15
(Use the shortest curve on the chart) In this instance due to there being two different SDR’s of pipes we have to apportion the additional creep allowance in proportion to the volumes of each of the pipes being tested.
PE and Steel
Size | Length | SDR | Factor |  | Time H/M | Conditioning Period |  | Conditioning Time |  | Total Test Time
450 | 195 | 21 | 0.1146 | 22.347 | 22:20
18" | 55 | 0 | 0.1344 | 7.392 | 07:23
|  |  |  | 29.739 | 29:44 | 6.8 | 4.3734 | 04:22 | 34.1124 | 34:06
Conditioning Period Table
SDR | PE | Pressure | Conditioning period |  |  | Additional Creep
11 | 80 | 7/5.5 | 1 |  |  | 9
11 | 80 | 6/4 | 1.6 |  |  | 9
11 | 100 | 7/7 | 2.3 |  |  | 8.6
26 | 80 | 3/2 | 2.4 |  |  | 8.5
21 | 80 | 3/2 | 3.5 |  |  | 7.5
17 | 80 | 3/2 | 4.9 |  |  | 6.5
21 | 100 | 3/2 | 6.8 |  |  | 5.4
11 | 80 | 3/2 | 9.4 |  |  | 4.4
Initial pressurisation |  |  | 2018-06-22 14:00
Test commenced |  |  | 2018-06-24 09:38
Total actual conditioning time |  |  | 43:38
Test on pressure |  |  | 4.1453
Test completed |  |  | 2018-06-25 14:49
Test off pressure |  |  | 4.1445
Total actual test duration |  |  | 29:11
Pressure drop |  |  | 0.0008
Total Creep Allowance |  |  | 1.743
Actual Test time |  |  | 43:38
Actual Conditioning time |  |  | 29:11
Total Volume |  |  | 33.15
Creep by Volume
| Volume | % Volume of test
Pipe 1 | 8.52 | 25.7014 | %
Pipe 2 | 24.63 | 74.2986 | %
| Factor | Allowable drop from curve | Actual drop
Pipe 1 | 0.66883 | 1 | 0.25701
Pipe 2 | 0.66883 | 2 | 1.486
Total Creep Allowance |  |  | 1.743

## Test_using_Volume
|  |  | 10mbar | 3mbar | PE Pipe 1 |  |  | Pipe id / 2 r |  | 0.1425
|  | LP | 1.0xV | 0.3xV | Pipe Diameter |  | 315 | r * r =r2 |  | 0.020306
[5 empty] | SDR | 21 | 30 | pi * r2 =a |  | 0.063802
|  | MP |  | .88xV | PE Type |  |  | a * L = v |  | 11.1654
[5 empty] | Pipe ID in m |  | 0.285 | v *.3 | 350 | 3.3496
|  | IP | 4bar | .84xV | Length in m | 175 |  | v *0.88 | 3 | 9.8255
|  |  | 5.5bar | 1.12xV | Total Volume in m3 | 11.1654 |  | v *0.84 | 4 | 9.3789
|  |  | 7bar | 1.75xV | Total Volume in Lts | 11165.3916 |  | v *1.12 | 5.5 | 12.5052
[5 empty] | Total Volume Gallons | 2453.9322 |  | v *1.75 | 7 | 19.5394
Initial pressurisation |  |  | 2018-06-22 14:00
Test commenced |  |  | 2018-06-24 09:38
Total actual conditioning time |  |  | 43:38 | 43.6333
Test on pressure |  |  | 4.1453
Test completed |  |  | 2018-06-25 14:49
Test off pressure |  |  | 4.1445
Total actual test duration |  |  | 29:11 | 29.1833
Pressure drop |  |  | 0.0008
Total Creep Allowance |  |  | 1.743
Actual Test time |  |  | 43.6333
Actual Conditioning time |  |  | 29.1833
Total Volume |  |  | 33.15
Creep by Volume
| Volume | % Volume of test
Pipe 1 | 8.52 | 25.7014 | %
Pipe 2 | 24.63 | 74.2986 | %
| Factor | Allowable drop from curve | Actual drop
Pipe 1 | 0.66883 | 1 | 0.25701
Pipe 2 | 0.66883 | 2 | 1.486
Total Creep Allowance |  |  | 1.743

## Test Volumes
PE Pipe 1 |  |  | Pipe id / 2 r |  | 0.12886
Pipe Diameter |  | 315 | r * r =r2 |  | 0.016606
SDR | 11 | 57.2727 | pi * r2 =a |  | 0.052176
PE Type |  |  | a * L = v |  | 33.9141
Pipe ID in m |  | 0.25773 | v *.3 | 350 | 10.1742
Length in m | 650 |  | v *0.88 | 3 | 29.8444
Total Volume in m3 | 33.9141 |  | v *0.84 | 4 | 28.4878
Total Volume in Lts | 33914.1004 |  | v *1.12 | 5.5 | 37.9838
Total Volume Gallons | 7453.6485 |  | v *1.75 | 7 | 59.3497
PE Pipe 2 |  |  | Pipe id / 2 r |  | 0.1425
Pipe Diameter |  | 315 | r * r =r2 |  | 0.020306
SDR | 21 | 30 | pi * r2 =a |  | 0.063802
PE Type |  |  | a * L = v |  | 11.1654
Pipe ID in m |  | 0.285 | v *.3 | 350 | 3.3496
Length in m | 175 |  | v *0.88 | 3 | 9.8255
Total Volume in m3 | 11.1654 |  | v *0.84 | 4 | 9.3789
Total Volume in Lts | 11165.3916 |  | v *1.12 | 5.5 | 12.5052
Total Volume Gallons | 2453.9322 |  | v *1.75 | 7 | 19.5394
PE Pipe 3 |  |  | Pipe id / 2 r |  | 0.1425
Pipe Diameter |  | 315 | r * r =r2 |  | 0.020306
SDR | 21 | 30 | pi * r2 =a |  | 0.063802
PE Type |  |  | a * L = v |  | 11.1654
Pipe ID in m |  | 0.285 | v *.3 | 350 | 3.3496
Length in m | 175 |  | v *0.88 | 3 | 9.8255
Total Volume in m3 | 11.1654 |  | v *0.84 | 4 | 9.3789
Total Volume in Lts | 11165.3916 |  | v *1.12 | 5.5 | 12.5052
Total Volume Gallons | 2453.9322 |  | v *1.75 | 7 | 19.5394